## AR_5 _RB
CWSI AR-5 Repeater w/RB/RM-5 Relay Box Battery Load
Entries only to be made in the Yellow cell locations
Regulated Load in Standby
| Device Type |  | Qty | X | [Current Draw] | = | Total
| Main Circuit Board |  | 1 | X | .026 | = | 0.026
| RB Board (input number of relay boards |  | 0 | X | .002 | = | 0
| Total Regulated Standby Load |  |  |  |  | = | 0.026
Entries only to be made in the Yellow cell locations
Regulated Load in Alarm
| Device Type |  | Qty | X | [Current Draw] | = | Total
| Main Circuit Board |  | 1 | X | 0.18 | = | 0.18
| RB Board (input number of relay boards |  | 0 | X | 0.11 | = | 0
| RM-5 Modular Relay Board |  | 0 | X | 0.1 | = | 0
| NAC # 1 |  | 0 | X | 0 | = | 0
| NAC # 2 |  | 0 | X | 0 | = | 0
| Total Regulated Alarm Load |  |  |  |  | = | 0.18
Total Secondary Power Requirements at 24 DC
Required Standby Time
(24 or 60 hours)
| Total Regulated Standby Load | 0.026 | X |  | 24 | = | 0.624 | 0.624 | AH
Required Alarm Time
for 5 min enter .084, for 15 mins, enter 0.250
| Total Regulated Alarm Load | 0.18 | X |  | .084 | = | 0.01512 | AH
| Sum of Standby and Alarm Ampere Hours | [5 empty] | 0.63912 | AH
| Muiltiply by the Derating Factor |  |  |  | X |  | 1.2 | AH
| Battery Size/Total Amperes Required | [5 empty] | 0.76694 | AH
Battery Size = 4 aH | [6 empty] | The panel is capable of charging the selected batteries.