## CP-3000_3000D
CWSI CP-3500D Control Panel
Regulated Load in Standby
| Device Type |  | Qty | X | [Current Draw] | = | Total
| Main Circuit Board |  | 1 | X | .089 | = | 0.089
[6 empty] | = | 0
| Total Regulated Standby Load |  |  |  |  | = | 0.089
Entries to be made in yellow cells only
Regulated Load in Alarm
| Device Type |  | Qty | X | [Current Draw] | = | Total
| Main Circuit Board |  | 1 | X | 0.28 | = | 0.28
| NAC # 1 |  | 0 | X | 0 | = | 0
| NAC # 2 |  | 0 | X | 0 | = | 0
| Total Regulated Alarm Load |  |  |  |  | = | 0.28
Total Secondary Power Requirements at 24 DC
Required Standby Time
(24 or 60 hours)
| Total Regulated Standby Load | 0.089 | X |  | 24 | = | 2.136 | 2.136 | AH
Required Alarm Time
for 5 min enter .084, for 15 mins, enter 0.250
| Total Regulated Alarm Load | 0.28 | X |  | .084 | = | 0.02352 | AH
| Sum of Standby and Alarm Ampere Hours | [5 empty] | 2.1595 | AH
| Muiltiply by the Derating Factor |  |  |  | X |  | 1.2 | AH
| Battery Size/Total Amperes Required | [5 empty] | 2.5914 | AH
Battery Size = 4 aH | [6 empty] | The panel is capable of charging the selected batteries.